Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to CastleRock Exteriors, a division of CastleRock Building Products Inc. ("Licensee").

This independent Product MasterSpec Section uses original MasterSpec text.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit Project requirements.

For more information, contact CastleRock Exteriors, a division of CastleRock Building Products Inc., 300 East Franklin Rd., Meridian, ID 83642; Phone: (208) 895-8557; Fax: (208) 639-6422; Website: castlerockx.com; Email: info@castlerockx.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 074463 - FABRICATED FACED PANEL ASSEMBLIES

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

MasterSpec includes provisions for LEED 2009, LEED v4, IgCC, and Green Globes.

- GENERAL

      - SUMMARY

        - Section Includes:

          - Mechanically attached mortarless insulated fabricated porcelain-[tile-] faced siding panels.

          - Mechanically attached mortarless insulated fabricated tile-faced siding panels.

          - Accessories.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 061600 "Sheathing" for wall sheathing substrates.

Retain appropriate Section reference below for type of weather barrier or air barrier included in Project; delete Sections not used.

          - Section 072500 "Weather Barriers" for water-resistive barriers.

          - Section 072713 "Modified Bituminous Sheet Air Barriers" for vapor-retarding, modified bituminous sheet type air barriers.

          - Section 072715 "Nonbituminous Self-Adhering Sheet Air Barriers" for vapor-retarding and vapor-permeable nonbituminous sheet type air barriers.

          - Section 072726 "Fluid-Applied Membrane Air Barriers" for vapor-retarding and vapor-permeable fluid-applied air barriers.

      - PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

        - Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

If needed, insert list of conference participants not mentioned in Section 13100 "Project Management and Coordination."

Retain subparagraphs below if additional requirements are necessary; revise to include more specific information about conference.

          - Meet with Owner, Architect, fabricated faced panel Installer, fabricated faced panel manufacturer's representative, structural-support Installer, and installers whose work interfaces with or affects fabricated faced panel assembly, including installers of doors, windows, and louvers.

          - Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

          - Review methods and procedures related to fabricated faced panel assembly installation, including manufacturer's written instructions.

          - Examine support conditions for compliance with requirements, including alignment between and attachment to structural members.

          - Review flashings, special siding details, mockups, wall penetrations, openings, and condition of other construction that affect fabricated faced panel assembly.

          - Review temporary protection requirements for fabricated faced panel assembly during and after installation.

          - Review procedures for repair of fabricated faced panels damaged after installation.

          - Document proceedings, including corrective measures and actions required, and furnish copy of record to each participant.

      - ACTION SUBMITTALS

        - Product Data: For each type of product.

          - Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for each type of panel and accessory included in assembly.

        - Shop Drawings:

          - Include fabrication and installation layouts of fabricated faced panel assembly; details of edge conditions, joints, panel profiles, corners, anchorages, attachment system, trim, flashings, closures, and accessories; and special details.

          - Accessories: Include details of the flashing, trim, and anchorage systems, at a scale of not less than 1-1/2 inches per 12 inches (1:10).

        - Samples for Initial Selection: For each type of fabricated faced panel assembly indicated with factory-applied color finishes.

          - Samples for each facer unit required, showing full range of color and texture expected. Include Sample showing color and texture of joint treatment.

Retain "Grout Samples" Subparagraph below only if using grouted porcelain-tile- and porcelain-brick-faced panels in Project.

            - Grout Samples: If grout is to be used, color charts consisting of actual sections of grout showing manufacturer's full range of colors.

          - Include similar Samples of exposed trim and accessories involving color selection.

        - Samples for Verification: For each type of exposed finish, prepared on Samples a minimum of 12 inches (305 mm) long by 24 inches (609.6 mm) panel width. Include exposed trim and accessories involving color selection.

Retain "Grout Samples" Subparagraph below only if using grouted porcelain-tile- and porcelain-brick-faced panels in Project.

          - Grout Samples: Showing color and texture of joint treatment.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data: For Installer.

        - Product Test Reports: For each product, tests performed by a qualified testing agency.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - CLOSEOUT SUBMITTALS

        - Maintenance Data: For fabricated faced panel assembly to include in maintenance manuals.

      - QUALITY ASSURANCE

        - Installer Qualifications: An entity that employs installers and supervisors who are trained and approved by manufacturer.

        - Mockups: Build mockups to verify selections made under Sample submittals, to demonstrate aesthetic effects, and to set quality standards for fabrication and installation.

Retain first subparagraph below for large-scale mockup. Indicate portion of building represented by mockup on Drawings or draw mockup as separate element. Revise to suit Project or if larger mockup is needed for field performance testing.

          - Build mockup of typical fabricated faced panel assembly [as indicated on Drawings] <Insert size>, including[ corner,] supports, attachments, trim, and accessories.

          - Water-Spray Test: Conduct water-spray test of fabricated faced panel assembly mockup, testing for water penetration in accordance with AAMA 501.2.

Retain first subparagraph below if mockups are not only for establishing appearance factors.

          - Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

Retain subparagraph below if the intention is to make an exception to the default requirement in Section 014000 "Quality Requirements" for demolishing and removing mockups.

          - Subject to compliance with requirements, approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver components, fabricated faced panels, and other manufactured items so as not to be damaged or deformed. Package fabricated faced panels for protection during transportation and handling with manufacturer's name and identification of products.

        - Unload, store, and erect fabricated faced panels in a manner to prevent bending, warping, twisting, and surface damage. If in boxes on pallets, do not open boxes or pallets until ready to install.

        - Stack fabricated faced panels horizontally on platforms or pallets, covered with suitable weathertight and ventilated covering. Store fabricated faced panels to ensure dryness, with positive slope for drainage of water. Do not store fabricated faced panels in contact with other materials that might cause staining or other surface damage.

      - FIELD CONDITIONS

        - Weather Limitations: Proceed with installation only when existing and forecasted weather conditions permit assembly of fabricated faced panels to be performed in accordance with manufacturers' written instructions.

      - COORDINATION

        - Coordinate fabricated faced panel installation with rain drainage work, flashing, trim, and construction of other adjoining work to provide a leakproof, secure, and noncorrosive installation.

- PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

      - MATERIALS

        - Source Limitations: Obtain primary fabricated faced wall panel assembly materials and accessories from single-source manufacturer.

      - PERFORMANCE REQUIREMENTS

        - Structural Performance: Provide fabricated faced panel assembly systems capable of withstanding an ultimate load not less than 88 lb/sq. ft. (423 kg/sq. m), based on testing in accordance with ASTM E330.

        - Fire-Test-Response Characteristics: Provide fabricated faced wall panels and system components with the following fire-test-response characteristics, as determined by testing identical panels and system components per test method indicated below by UL, Intertek Laboratories, Warnock Hersey, or another testing and inspecting agency acceptable to Authorities Having Jurisdiction (AHJ). Identify products with appropriate markings from an applicable testing agency.

Subparagraphs below are examples only; revise to suit Project after verifying requirements of authorities having jurisdiction (AHJ).

Retain "Fire-Resistance Characteristics" Subparagraph below only where fire-resistance-rated wall construction is required. Verify acceptability of such assemblies with AHJ.

          - Fire-Resistance Characteristics: Provide materials and construction tested for fire resistance per ASTM E119.

          - Radiant Heat Exposure: No ignition when tested in accordance with NFPA 268.

          - Potential Heat: Acceptable level when tested in accordance with NFPA 259.

          - Surface-Burning Characteristics: Provide fabricated faced wall panels with a flame-spread index of zero and a smoke-developed index of zero, per ASTM E84.

      - Mechanically attached Mortarless insulated fabricated porcelain or DEKTON -[Tile-] faced siding panels <Insert drawing designation>

Copy paragraphs below and re-edit for each type of siding panel required. Insert number to complete drawing designation. Use these designations on Drawings to show where each siding panel type is required.

        - Description: Pre-engineered insulated faced-siding panel system designed for anchoring to suitable substrates with concealed fasteners. Panels consist of the assemblage of components as specified below.

CastleRock Exteriors offers their Porcelain-Tile-Faced Panel System in four Series: "PFP" for flush, nongrouted and grouted panels; and "PLP" for lap-siding panels; Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

- Basis-of-Design Product: Subject to compliance with requirements, provide CastleRock Exteriors; ICAP-USA Exterior Continuous Insulated Porcelain for Dekton-[Tile-] Faced Panel System, Series [PFP] [PLP]  or comparable product by one of the following:

At the time of this writing, there are no direct competitors for these types of fabricated porcelain-tilebrick-faced panel assemblies.

            - <Insert manufacturer's name>.

CastleRock Exteriors uses porcelain-tile  from a variety of manufacturers. Coordinate product information below with porcelain-material facers selected for Project. Thicker tiles may be required if using "Large Format" sized porcelain or Dekton-tiles. Coordinate selected dimensional information below with porcelain-material manufacturer.

          - Porcelain-[Tile] Facers: Impervious vitreous tile conforming to the requirements of ANSI A137.1, with a water-absorption rate of 0.5 percent or less in accordance with ASTM C373 test method; abrasion, freeze/thaw, chemical, and stain resistant; intended for exterior use. Facers are bonded to insulated backer panels with the manufacturer’s proprietary silicone adhesive.

            - Facer Size: <Insert dimensions>.

            - Facer Thickness: [1/4 inch (6.4 mm)][5/16 inch (8.0 mm] [3/8 inch (9.5 mm)] <Insert dimension>.

            - Colors and Textures: [As indicated by manufacturer's designations] [Match Architect's samples] [As selected by Architect from manufacturer's standard range] [As selected by Architect from manufacturer's custom range] [As selected by Architect from manufacturer's full standard and custom range] <Insert color and texture>.

              - Blending: For porcelain-[tile] facers exhibiting color variations, verify that facers have been factory blended and packaged so units taken from one package show same range of colors as those taken from other packages and match approved Samples. If not factory blended, either return to manufacturer or blend facers at Project site before installing.

          - Insulated Backer Panels: High-density molded (expanded) polystyrene board insulation, ASTM C578, Type XV, 60-psi (414-kPa) minimum compressive strength; with interlocking, machined tongue-and-groove perimeter.

            - Thermal Resistivity: R-Value of [5] [10] [21].

Thicknesses listed in "Backer Panel Thickness" Subparagraph below pertain to R-Value selected in "Thermal Resistivity" Subparagraph above in the same respective order.

            - Backer Panel Thickness: [2 inches (50.8 mm)] 1 inches (25.4 mm)][4 inches (102 mm)].

            - Overall Panel Size: [6 by 36 inches (152 by 914 mm)] [8 by 36 inches (203 by 914 mm)] [6 by 48 inches (152 by 1219 mm)] [8 by 48 inches (203 by 1219 mm)] [24 by 48 inches (610 by 1219 mm)] [23.6 by 23.6 inches (600 by 600 mm)] [23.6 by 47.2 inches (600 by 1200 mm)] [15.75 by 47.2 inches (400 by 1200 mm)] <Insert dimensions [max. 24 inches  by 126 inches (609 by 3,200 mm) ]>.

          - Special Shapes: Manufacturer Starter metal. Lashing materials provided by others to match finish colors.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances, fabricated faced panel supports, and other conditions affecting performance of the Work.

          - Examine wall framing to verify that support members and anchorage have been installed within alignment tolerances required by fabricated faced panel manufacturer.

          - Examine wall sheathing to verify that sheathing joints are supported by framing or blocking and that installation is within flatness tolerances required by fabricated faced panel manufacturer.

          - Verify that air- or water-resistive barriers have been installed over sheathing or backing substrate to prevent air infiltration or water penetration.

        - Examine roughing-in for components and systems penetrating fabricated faced panels to verify actual locations of penetrations relative to seam locations of fabricated faced panels before installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - FABRICATED FACED PANEL ASSEMBLY INSTALLATION

        - General: Install fabricated faced panel assembly in accordance with manufacturer's written instructions in orientation, sizes, and locations indicated. Anchor fabricated faced panel assembly and other components of the Work securely in place, with provisions for thermal and structural movement.

          - Shim or otherwise plumb substrates receiving fabricated faced panels.

          - Flash and seal fabricated faced panels at perimeter of all openings. Do not begin panel installation until air- or water-resistive barriers and flashings that will be concealed by fabricated faced panels are installed.

          - Install flashing and trim as fabricated faced panel work proceeds.

          - Align bottoms of fabricated faced panels.

          - Provide weathertight escutcheons for pipe- and conduit-penetrating panels.

        - Metal Protection: Where dissimilar metals contact each other or corrosive substrates, protect against galvanic action as recommended in writing by fabricated faced panel manufacturer.

Retain "Grouting" Subparagraph below only if using grouted porcelain-tile- and porcelain-brick-faced panels in Project.

        - Grouting: Install grout in accordance with ANSI A108.10. Completely fill joints between porcelain-[tile] [brick] facers with grout, and compress into place without spreading grout onto exposed surfaces of facers. Remove excess grout immediately to prevent staining of facers.

Retain joint profile from options in first subparagraph below or revise to suit Project. Joint shapes are listed in order of decreasing weathertightness in accordance with BIA Technical Note 21C.

          - Tool joints to a [slightly concave] [V-]shape when grout is thumbprint hard.

          - Clean exposed surfaces and joints of grouted facers.

        - Accessory Installation: Install accessories with positive anchorage to building and weathertight mounting, and provide for thermal expansion. Coordinate installation with flashings and other components.

        - Flashing and Trim: Comply with performance requirements, manufacturer's written installation instructions, and SMACNA's "Architectural Sheet Metal Manual." Provide concealed fasteners where possible, and set units true to line and level. Install work with laps, joints, and seams that are permanently watertight.

          - Install exposed flashing and trim that is without buckling and tool marks, and that is true to line and levels indicated, with exposed edges folded back to form hems. Install sheet metal flashing and trim to fit substrates and to achieve waterproof performance.

          - Expansion Provisions: Provide for thermal expansion of exposed flashing and trim. Space movement joints at building expansion joint locations as specified by the architect.

          - Provide expansion joints at building expansion locations, at every floor level expansion joint, and as recommended in manufacturer's written installation instructions.

        - Joint Sealers: Install joint fillers and sealants where indicated and where required for weathertight performance of fabricated faced wall panel assemblies.

Retain subparagraph below if joint-sealant work is part of this Section.

          - Prepare joints and apply sealants to comply with requirements in Section 079200 "Joint Sealants."

      - FIELD QUALITY CONTROL

Retain "Testing Agency" Paragraph below to identify who shall perform tests and inspections. If retaining second option below, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency: Owner will engage a qualified testing agency to perform tests and inspections.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Fabricated faced panels will be considered defective if they do not pass test and inspections.

        - Additional tests and inspections, at Contractor's expense, are performed to determine compliance of replaced or additional work with specified requirements.

        - Prepare test and inspection reports.

      - CLEANING AND PROTECTION

        - Remove temporary protective coverings and strippable films, if any, as fabricated faced panels are installed, unless otherwise indicated in manufacturer's written installation instructions. On completion of fabricated faced panel installation, clean finished surfaces as recommended by manufacturer. Maintain in a clean condition during construction.

        - After fabricated faced panel assembly installation, clear weep holes and drainage channels of obstructions, dirt, and sealant.

        - Replace fabricated faced panels that have been damaged or have deteriorated beyond successful repair by finish touchup or similar minor repair procedures.

END OF SECTION 074463